## 1 - HW Main Meter Power
Questions for Ops: | A lot of these events line up with 3 - HW Main Meter Flow indicating they are likely related to operations. The sensor also has a lot of spikes, potentially most of these events are not anomalies. Very subjective.
Timestep Recommendation: | Minimum daily windows to capture daily pattern - likely going with a 2-3 minimum day window is better. The data is ~minute data so would correspond with a minimum of 1500-4500 points.
Timestep Figures: | 1_step_a
General Figures: | 1_all_a, 1_all_b
Photo # | Comment | Type Estimate | Date | Related to
1a | Several points drop to zero (even though the trend is going down) | System | 2020-01-08 | Lines up with 3 - HW Main Meter Flow
1b | Points at zero | Sensor? | 2020-03-15 | Lines up with 3 - HW Main Meter Flow
1c | Points drop to zero | System | 2020-03-25 | Lines up with 3 - HW Main Meter Flow
1d | Points drop to zero rapidly | System | 2020-04-10 | Lines up with 3 - HW Main Meter Flow
1e | Points go down to zero and back up, on and off | System | 2020-05-08 | Lines up with 3 - HW Main Meter Flow
1f | Points rapidly drop to zero | System | 2020-07-03 | Lines up with 3 - HW Main Meter Flow
1g | Points rapidly drop to zero | System | 2020-07-14
1h | Points rapidly drop to zero | System | 2020-07-26
1i | Points rapidly drop to zero | System | 2020-08-07
1j | Points rapidly drop to zero | System | 2020-08-09
1k | Points rapidly drop to zero | System | 2020-08-25 | Lines up with 3 - HW Main Meter Flow
1l | Points rapidly drop to zero | System | 2020-09-06
1m | Points rapidly drop to zero | System | 2020-10-07
1n | Rapid spike and drop to zero | System | 2020-11-27
1o | Points near zero | Sensor? | 2020-12-13 | Lines up with 3 - HW Main Meter Flow
1p | Rapid drop to near zero | System | 2020-12-22 | Lines up with 3 - HW Main Meter Flow
1q | Point well below trend | Sensor? | 2020-12-30 | Lines up with 3 - HW Main Meter Flow
1r | Large spike dropping to near zero | System | 2021-01-02 | Lines up with 3 - HW Main Meter Flow
1s | Large spike | System | 2021-02-03 | Lines up with 3 - HW Main Meter Flow
1t | Large spike | System | 2021-02-12 | Lines up with 3 - HW Main Meter Flow
1u | Large spike dropping to near zero | System | 2021-04-19
1v | Large spike dropping to near zero | System | 2021-05-05 | Lines up with 3 - HW Main Meter Flow

## 2 - HW Main Meter Entering Wate
Questions for Ops: | - There are periods in the summer of 2017, 2018, 2019 (but not in 2020) that have very distinct patterns compared with the rest of the tract - is this considered normal or are there potential issues with the data or operations? See images 2_q_a, 2_q_b, 2_q_c, 2_q_d. - There are also large spikes with temp drop/increases not near these summer periods, is this normal, or does it represent abnormal operations or potential issues with sensors? See images 2_q_e, 2_q_f.
Timestep Recommendation: | Minimum daily windows to capture daily pattern - likely going with a 2-3 minimum day window is better. The data is 15min data so would correspond with a minimum of 100-300 points.
Timestep Figures: | 2_step_a
General Figures: | 2_all_a
Photo # | Comment | Type Estimate | Date
2a | Points with zero values | Sensor | Various
2b | Points sitting high above trend | Sensor? | 2018-10-26
2c | Flatline data | Sensor | Various, Dec 2018-Jan2019
2d | Points sitting high above trend | Sensor? | 2020-03-25
2e | Points sitting high above trend | Sensor? | 2020-04-10
2f | Cluster of points high above trend | Sensor | 2020-05-24
2g | Points sitting high above trend | Sensor | 2020-08-04
2h | Points sitting high above trend | Sensor | 2020-08-18
2i | Points sitting high above trend | Sensor | 2021-05-05
2j | Sharp drop in points | System? | 2021-02-06
2k | Points drop well below trend | System | 2021-01-07
2l | Sharp drop in points | System? | 2021-04-17
2l | Sharp drop in points | System? | 2021-04-18

## 3 - HW Main Meter Flow
Questions for Ops: | No specific questions on this sensor. If possible would be good to get ops to comment/validate. A lot of these events line up with 1 - HW Main Meter Power indicating they are likely related to operations.
Timestep Recommendation: | Minimum daily windows to capture daily pattern - likely going with a 2-3 minimum day window is better. The data is ~minute data so would correspond with a minimum of 1500-4500 points.
Timestep Figures: | 3_step_a, 3_step_b
General Figures: | 3_all_a, 3_all_b
Photo # | Comment | Type Estimate | Date | Related to
3a | Several points drop to zero | System | 2020-01-08 | Lines up with 1 - HW Main Meter Power
3b | Groups of points appear to jump above trend - may not be an anomaly | System | 2020-02-07 | Trend shows up on 1 - HW Main Meter Power
3c | Single point sitting well above trend | Sensor | 2020-02-21
3d | Points drop to zero rapidly | Sensor? | 2020-03-15 | Lines up with 1 - HW Main Meter Power
3e | Points drop to zero rapidly | System | 2020-03-25 | Lines up with 1 - HW Main Meter Power
3f | Points drop to zero rapidly | System | 2020-04-10 | Lines up with 1 - HW Main Meter Power
3g | Points go down to zero and back up | System | 2020-05-08 | Lines up with 1 - HW Main Meter Power
3h | Points spike up and down | System | 2020-07-03 | Lines up with 1 - HW Main Meter Power
3i | Point near zero below trend | System | 2020-08-25 | Lines up with 1 - HW Main Meter Power
3j | Point well below trend | Sensor | 2020-11-09
3k | Points spike up and down | System | 2020-11-27 | Lines up with 1 - HW Main Meter Power
3l | Points drop to zero rapidly | Sensor? | 2020-12-13 | Lines up with 1 - HW Main Meter Power
3m | Flatline of points above trend | Sensor | 2020-12-18
3n | Points drop to zero and go back up | System | 2020-12-22 | Lines up with 1 - HW Main Meter Power
3o | Points spike up and down | Sensor? | 2020-12-30 | Lines up with 1 - HW Main Meter Power
3p | Points spike up and down | System | 2021-01-02 | Lines up with 1 - HW Main Meter Power
3q | Points spike up and down | System | 2021-02-03 | Lines up with 1 - HW Main Meter Power
3r | Points spike up and down | System | 2021-02-12 | Lines up with 1 - HW Main Meter Power
3s | Points spike up and down | System | 2021-05-05 | Lines up with 1 - HW Main Meter Power

## 4 - Boiler B-1 Gas Pressure
Questions for Ops: | Are dips in winter time of concern? Spread in the winter becomes larger on sensor, is that regular behaviour?
Timestep Recommendation: | Minimum daily windows to capture daily pattern - likely going with a 7 minimum day window is better. The data is ~15 minute data so would correspond with a minimum of 672 points.
Timestep Figures: | 4_step_a
General Figures: | 4_all_a
Photo # | Comment | Type Estimate | Date
4a, 4b | Spike in several points | Sensor | 2020-01-08
4b | Spike in several points | Sensor | 2020-01-10
4b | Spike in several points | Sensor | 2020-01-17
4c | Drop in pressure | System? | 2020-01-13
4d | Spike in several points | Sensor | 2020-03-18
4d | Spike in several points | Sensor | 2020-03-22
4d | Spike in several points | Sensor | 2020-03-25
4e | Spike in several points | Sensor | 2020-04-09
4e | Spike in several points | Sensor | 2020-04-10
4f | Spike in several points | Sensor | 2020-05-10
4g | Spike in several points | Sensor | 2020-07-17
4h | Spike in several points | Sensor | 2020-07-27
4j | Spike in several points | Sensor | 2020-08-10
4k | Spike in several points | Sensor | 2020-09-01
4l | Spike in several points | Sensor | 2020-09-17
4l | Spike in several points | Sensor | 2020-09-18
4m | Spike in several points | Sensor | 2020-09-25
4n | Spike in several points | Sensor | 2020-10-07
4n | Spike in several points | Sensor | 2020-10-08
4o | Spike in several points | Sensor | 2020-11-25
4p | Drop in pressure /w Spike | Sensor/System | 2020-12-21
4q | Spike in several points | Sensor | 2021-02-03
4r | Drop in pressure /w Spike | Sensor/System | 2021-02-08
4s | Spike in several points | Sensor | 2021-02-25
4t | Spike in several points | Sensor | 2021-03-28

## 5 - Boiler B-1 Exhaust O2
Questions for Ops: | No specific questions on this sensor. If possible would be good to get ops to comment/validate.
Timestep Recommendation: | Minimum daily windows to capture daily pattern - likely going with a 7 minimum day window is better. The data is ~15 minute data so would correspond with a minimum of 672 points.
Timestep Figures: | 5_step_a
General Figures: | 5_all_a
Photo # | Comment | Type Estimate | Date
5a | Sudden zero reading. | Sensor | 2020-01-16
5b | Spike and drop in reading. | System? | 2020-01-31
5c | Spike and drop in reading. | System? | 2020-10-22
5d | Spike and several zero readings | Sensor/System? | 2020-10-28
5e | Sudden zero reading. | Sensor | 2020-11-12