## CEC Boiler B-1 Exhaust O2
Dataset | Description | Model Description | Window Points | Approx Window Timeframe (hr) | Patience | Model Runtime (min) | Notes | Thresholds Looked At | Estimated Best Threshold | General Comments | Pictures
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 4 | 1 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Catches most jump anomalies - Short window prevents from anomalies from dragging on | data_5a_PD_ts_4_thresh_25_a data_5a_PD_ts_4_thresh_25_b data_5a_PD_ts_4_thresh_25_c data_5a_PD_ts_4_thresh_50_a data_5a_PD_ts_4_thresh_50_b data_5a_PD_ts_4_thresh_75_a
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 8 | 2 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Catches most jump anomalies (couple less than 4 window) | data_5a_PD_ts_8_thresh_25_a data_5a_PD_ts_8_thresh_25_b data_5a_PD_ts_8_thresh_25_c data_5a_PD_ts_8_thresh_50_a data_5a_PD_ts_8_thresh_50_b data_5a_PD_ts_8_thresh_75_a
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 48 | 12 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Catches most jump anomalies (couple less than 4 window) - PD prediction in general prevents anomalies from dragging on | data_5a_PD_ts_48_thresh_25_a data_5a_PD_ts_48_thresh_25_b data_5a_PD_ts_48_thresh_25_c data_5a_PD_ts_48_thresh_50_a data_5a_PD_ts_48_thresh_75_a
CEC_compiled_data_5a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 4 | 1 | 10 | <2 | No significant difference from all data | 0.25, 0.5, 0.75 | 0.25 | - Very little difference from non-normal data | data_5a_PD_norm_ts_4_thresh_25_a data_5a_PD_norm_ts_4_thresh_25_b data_5a_PD_norm_ts_8_thresh_25_c
CEC_compiled_data_5a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 8 | 2 | 10 | <2 | No significant difference from all data | 0.25, 0.5, 0.75 | 0.25 | - Very little difference from non-normal data | data_5a_PD_ts_8_thresh_25_a data_5a_PD_ts_8_thresh_25_b data_5a_PD_ts_8_thresh_25_c
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 4 | 1 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Catches most jump anomalies - Short window prevents from anomalies from dragging on | data_5a_SW_ts_4_thresh_25_a data_5a_SW_ts_4_thresh_25_b data_5a_SW_ts_4_thresh_25_c data_5a_SW_ts_4_thresh_50_a data_5a_SW_ts_4_thresh_50_b data_5a_SW_ts_4_thresh_75_a
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 8 | 2 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Catches more contextual anomalies. Misses a couple jumps (more than 4) - Longer window starts dragging on anomalies | data_5a_SW_ts_8_thresh_25_a data_5a_SW_ts_8_thresh_25_b data_5a_SW_ts_8_thresh_25_c data_5a_SW_ts_8_thresh_50_a data_5a_SW_ts_8_thresh_50_b data_5a_SW_ts_8_thresh_75_a
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 48 | 12 | 10 | <2 |  | 0.25, 0.5, 0.75 | 0.25 | - Misses quite a few anomlies - Longer window starts drags in long sequences | data_5a_SW_ts_48_thresh_25_a data_5a_SW_ts_48_thresh_25_b data_5a_SW_ts_48_thresh_25_c data_5a_SW_ts_48_thresh_50_a data_5a_SW_ts_48_thresh_75_a
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 4 | 1 | 10 | <2 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Catches more contextual anomalies. Misses a couple jumps (more than 4) - Longer window starts dragging on anomalies | data_5a_ts_4_thresh_25_a data_5a_ts_4_thresh_25_b data_5a_ts_4_thresh_33_a data_5a_ts_4_thresh_33_b data_5a_ts_4_thresh_50_a data_5a_ts_4_thresh_50_b
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 6 | 1.5 | 10 | <2 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Catches almost all human identified anomalies - Identifies more tp and fp (potentially) than 4 window | data_5a_ts_6_thresh_25_a data_5a_ts_6_thresh_25_b data_5a_ts_6_thresh_33_a data_5a_ts_6_thresh_33_b
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 32 | 8 | 10 | <2 | This was supposed to be 24 hours but clearly messed up the math | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Catches most large jumps but misses smaller anomalies | data_5a_ts_32_thresh_25_a data_5a_ts_32_thresh_25_b data_5a_ts_32_thresh_33_a data_5a_ts_32_thresh_33_b
CEC_compiled_data_5a_updated.csv | No Anomalies Labelled | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 228 | 57 | 10 | <2 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Catches most large jumps but misses smaller anomalies - Some anomaly windows too long | data_5a_ts_228_thresh_25_a data_5a_ts_228_thresh_25_b data_5a_ts_228_thresh_33_a data_5a_ts_228_thresh_33_b
CEC_compiled_data_5a_updated.csv | Normal Training Data | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 4 | 1 | 10 | <2 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Similar to non-normal training data - Seems to be missing a couple anomalies | data_5a_norm_ts_4_thresh_25_a data_5a_norm_ts_4_thresh_25_b data_5a_norm_ts_4_thresh_33_a data_5a_norm_ts_4_thresh_33_b
CEC_compiled_data_5a_updated.csv | Normal Training Data | Model C: Train [a,b,c] -> c: predicts anomaly on mean([a,b,c]) | 6 | 1.5 | 10 | <2 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Similar to non-normal training data - Seems to be missing a couple anomalies | data_5a_norm_ts_6_thresh_25_a data_5a_norm_ts_6_thresh_25_b data_5a_norm_ts_6_thresh_33_a data_5a_norm_ts_6_thresh_33_b

## CEC HW Main Meter Power
Dataset | Description | Model Description | Window Points | Approx Window Timeframe (hr) | Patience | Model Runtime (min) | Notes | Thresholds Looked At | Estimated Best Threshold | General Comments | Pictures
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 15 | 0.25 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.33 | - Catches most jump anomalies - Doesn't catch entire events | data_1a_PD_ts_15_thresh_25_a data_1a_PD_ts_15_thresh_25_b data_1a_PD_ts_15_thresh_25_c data_1a_PD_ts_15_thresh_25_d data_1a_PD_ts_15_thresh_25_e data_1a_PD_ts_15_thresh_33_a data_1a_PD_ts_15_thresh_33_b data_1a_PD_ts_15_thresh_33_c data_1a_PD_ts_15_thresh_33_d data_1a_PD_ts_15_thresh_33_e data_1a_PD_ts_15_thresh_33_f data_1a_PD_ts_15_thresh_50_a
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 30 | 0.5 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.25-0.33 | - Catches most jump anomalies (couple less than 15 window) - Doesn't catch entire events - Seems to work slightly better than 15 point window | data_1a_PD_ts_30_thresh_25_a data_1a_PD_ts_30_thresh_25_b data_1a_PD_ts_30_thresh_25_c data_1a_PD_ts_30_thresh_25_d data_1a_PD_ts_30_thresh_25_e data_1a_PD_ts_30_thresh_25_f data_1a_PD_ts_30_thresh_33_a data_1a_PD_ts_30_thresh_50_a
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 60 | 1 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.25-0.33 | - Catches most jump anomalies - Doesn't catch entire events - Very similar to the 30 point window | data_1a_PD_ts_60_thresh_25_a data_1a_PD_ts_60_thresh_25_b data_1a_PD_ts_60_thresh_25_c data_1a_PD_ts_60_thresh_25_d data_1a_PD_ts_60_thresh_25_e data_1a_PD_ts_60_thresh_25_f data_1a_PD_ts_60_thresh_25_g data_1a_PD_ts_60_thresh_33_a data_1a_PD_ts_60_thresh_50_a
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 120 | 2 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.33-0.50 | - Catches most jump anomalies (catches the most for each threshold) - Doesn't catch entire events - Seems a bit too long of a window. | data_1a_PD_ts_120_thresh_25_a data_1a_PD_ts_120_thresh_25_b data_1a_PD_ts_120_thresh_25_c data_1a_PD_ts_120_thresh_25_d data_1a_PD_ts_120_thresh_25_e data_1a_PD_ts_120_thresh_25_f data_1a_PD_ts_120_thresh_25_g data_1a_PD_ts_120_thresh_33_a data_1a_PD_ts_120_thresh_33_b data_1a_PD_ts_120_thresh_33_c data_1a_PD_ts_120_thresh_33_d data_1a_PD_ts_120_thresh_33_e data_1a_PD_ts_120_thresh_33_f data_1a_PD_ts_120_thresh_33_g data_1a_PD_ts_120_thresh_50_a
CEC_compiled_data_1a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 15 | 0.25 | 10 | <5 | No significant difference from all data | 0.25, 0.5, 0.75 | n/a | - Very little difference from non-normal data | data_1a_PD_norm_ts_15_thresh_25_a data_1a_PD_norm_ts_15_thresh_25_b
CEC_compiled_data_1a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 120 | 2 | 10 | <5 | No significant difference from all data | 0.25, 0.5, 0.75 | n/a | - Very little difference from non-normal data | data_1a_PD_norm_ts_120_thresh_25_a data_1a_PD_norm_ts_120_thresh_25_b
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 15 | 0.25 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.25 | - Catches large anomalies but window seems too small to catch smaller ones | data_1a_SW_ts_15_thresh_25_a data_1a_SW_ts_15_thresh_33_a
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 30 | 0.5 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.33 | - Catches most event anomlies. - Might label too many points near event - Seems to perform quite well | data_1a_SW_ts_30_thresh_25_a data_1a_SW_ts_30_thresh_33_a data_1a_SW_ts_30_thresh_33_b data_1a_SW_ts_30_thresh_33_c data_1a_SW_ts_30_thresh_33_d data_1a_SW_ts_30_thresh_33_e data_1a_SW_ts_30_thresh_33_f data_1a_SW_ts_30_thresh_33_g data_1a_SW_ts_30_thresh_33_h
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 60 | 1 | 10 | <5 |  | 0.25, 0.33, 0.5, 0.75 | 0.33 | - Catches most event anomlies. - Might label too many points near event - Could perform better than 30 point window with some threshold tuning. | data_1a_SW_ts_60_thresh_25_a data_1a_SW_ts_60_thresh_33_a data_1a_SW_ts_60_thresh_33_b
CEC_compiled_data_1a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 120 | 2 | 10 | <5 |  | 0.25, 0.33, 0.65 | 0.65 | - Catches large anomaly events - Misses some point events and some other labelled - Seems a bit too long of a window. | data_1a_SW_ts_120_thresh_25_a data_1a_SW_ts_120_thresh_33_a data_1a_SW_ts_120_thresh_65_a data_1a_SW_ts_120_thresh_65_b data_1a_SW_ts_120_thresh_65_c data_1a_SW_ts_120_thresh_65_d

## CEC HW Main Meter Flow
Dataset | Description | Model Description | Window Points | Approx Window Timeframe (hr) | Patience | Model Runtime (min) | Notes | Thresholds Looked At | Estimated Best Threshold | General Comments | Pictures
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 15 | 0.25 | 10 | 5 | Probably lower patience by 5 | 0.25, 0.33, 0.5, 0.75 | 0.33 | - Catches most jump anomalies - Doesn't catch entire events | data_3a_PD_ts_15_thresh_25_a data_3a_PD_ts_15_thresh_25_b data_3a_PD_ts_15_thresh_25_c data_3a_PD_ts_15_thresh_25_d data_3a_PD_ts_15_thresh_25_e data_3a_PD_ts_15_thresh_25_f data_3a_PD_ts_15_thresh_25_g data_3a_PD_ts_15_thresh_33_a data_3a_PD_ts_15_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 30 | 0.5 | 10 | 6 | Probably lower patience by 6 | 0.25, 0.33, 0.65 | 0.25-0.33 | - Catches most jump anomalies (couple less than 15 window) - Doesn't catch entire events - Seems to work slightly better than 15 point window | data_3a_PD_ts_30_thresh_25_a data_3a_PD_ts_30_thresh_33_a data_3a_PD_ts_30_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 60 | 1 | 10 | 8 | Probably lower patience by 7 | 0.25, 0.33, 0.65 | 0.25-0.33 | - Catches most jump anomalies - Doesn't catch entire events - Very similar to the 30 point window | data_3a_PD_ts_60_thresh_25_a data_3a_PD_ts_60_thresh_25_b data_3a_PD_ts_60_thresh_25_c data_3a_PD_ts_60_thresh_25_d data_3a_PD_ts_60_thresh_25_e data_3a_PD_ts_60_thresh_33_a data_3a_PD_ts_60_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model A: Train [a,b,c] -> d: predicts anomaly on d | 120 | 2 | 10 | 12 | Probably lower patience by 8 | 0.25, 0.33, 0.65 | 0.33-0.50 | - Catches most jump anomalies (catches the most for each threshold) - Doesn't catch entire events - Seems a bit too long of a window. | data_3a_PD_ts_120_thresh_25_a data_3a_PD_ts_120_thresh_25_b data_3a_PD_ts_120_thresh_33_a data_3a_PD_ts_120_thresh_50_a
CEC_compiled_data_3a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 15 | 0.25 | 10 | 5 | No significant difference from all data | 0.25, 0.33, 0.65 | n/a | - Very little difference from non-normal data | data_3a_PD_norm_ts_15_thresh_25_a data_3a_PD_norm_ts_15_thresh_33_a data_3a_PD_norm_ts_15_thresh_65_a
CEC_compiled_data_3a_updated.csv | Normal Training Data | Model A: Train [a,b,c] -> d: predicts anomaly on d | 60 | 2 | 10 | 5 | No significant difference from all data | 0.25, 0.33, 0.65 | n/a | - Very little difference from non-normal data | data_3a_PD_norm_ts_60_thresh_25_a data_3a_PD_norm_ts_60_thresh_33_a data_3a_PD_norm_ts_60_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 15 | 0.25 | 10 | 2 |  | 0.25, 0.33, 0.65 | 0.25 | - Catches most event anomlies. - Shorter window would work better with real-time predictions. | data_3a_SW_ts_15_thresh_25_a data_3a_SW_ts_15_thresh_25_b data_3a_SW_ts_15_thresh_25_c data_3a_SW_ts_15_thresh_25_d data_3a_SW_ts_15_thresh_25_e data_3a_SW_ts_15_thresh_33_a data_3a_SW_ts_15_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 60 | 1 | 10 | 1 |  | 0.25, 0.33, 0.65 | 0.65 | - Catches most event anomlies. - Needs a higher threshold to limit out non-anomalous - Unsure whether results would be better than shorter window. | data_3a_SW_ts_60_thresh_25_a data_3a_SW_ts_60_thresh_33_a data_3a_SW_ts_60_thresh_65_a
CEC_compiled_data_3a_updated.csv | No Anomalies Labelled | Model B: [a,b,c] -> [a,b,c]: predicts anomaly on mean([a,b,c]) | 120 | 2 | 10 | 1 |  | 0.25, 0.33, 0.65 | >0.65 | - Catches most event anomlies. - Needs a higher threshold to limit out non-anomalous - Unsure whether results would be better than shorter window. | data_3a_SW_ts_120_thresh_25_a data_3a_SW_ts_120_thresh_33_a data_3a_SW_ts_120_thresh_65_a
CEC_compiled_data_3a_updated.csv
CEC_compiled_data_3a_updated.csv
CEC_compiled_data_3a_updated.csv